Environmental Mitigation and Monitoring Plan (EMMP)

## PROJECT/ACTIVITY DATA

| Project/Activity Name: | USAID Water and Sanitation Project – Charpentier Pumping Station QIP (Quick Impact Project) |
| --- | --- |
| Geographic Location(s) (Country/Region): | HAITI/LAC |
| Implementation Start/End: | 12/04/2017 – 06/05/2022 |
| Contract/Award Number: | AID-OAA-I-14-00049/720521 |
| Implementing Partner(s): | DAI GLOBAL, LLC |
| Tracking ID/link: |  |
| Tracking ID/link of Related IEE: | LAC-IEE-17-28 https://ecd.usaid.gov/repository/pdf/50023.pdf |
| Tracking ID/link of Other, Related Analyses: |  |

## ORGANIZATIONAL/ADMINISTRATIVE DATA

| Implementing Operating Unit(s): (e.g. Mission or Bureau or Office) | Office of Infrastructure, Energy and Engineering (OIEE) |
| --- | --- |
| Lead BEO Bureau: | Latin America and the Caribbean |
| Prepared by: | Tom Erdmann, Noé Destin, DAI GLOBAL, LLC |
| Date Prepared: | 1/22/2019 |
| Submitted by: | Sinan Al Najjar, DAI GLOBAL, LLC |
| Date Submitted: | 1/22/2019 |

## ENVIRONMENTAL COMPLIANCE REVIEW DATA

| Analysis Type: | EMMP |
| --- | --- |
| Additional Analyses/Reporting Required: | EMMR |

### purpose

The USAID Water and Sanitation project will work to ensure sustainable, safely managed, and affordable water and sanitation services to stem the spread of cholera and other waterborne diseases in Haiti.  The project will lay the foundation for a long-term, sustained effort to increase access to safe drinking water and sanitation in Haiti, where many communities suffer from high incidences of cholera and diarrheal diseases.  The purpose of this EMMP is to ensure that the ADS 204.3 requirements for incorporating and monitoring appropriate mitigation measures into project or activity design are implemented.  The mitigation measures in this EMMP respond to the LAC-IEE-17-28 “Negative determination, with Conditions.”

### USAID Approval of EMMP

PROJECT/ACTIVITY NAME: USAID WATER AND SANITATION PROJECT: Charpentier Pumping Station QIP

Clearance:; _CID__________________________________________ Marcia Urquhart Glenn, COR; _3/15/2019 Date. Clearance:; _CLEARED by e-mail______________________________ Abdel Abellard, Mission Environmental Officer; ______________ Date. Clearance:; CLEARED by email________________________________ Diana Shannon, Acting Regional Environmental Advisor; __4/8/2019_____ Date. Clearance:; CLEARED by e-mail________________________________ Karen d'Aboville, Resident Legal Officer; 4/9/2019_______ Date. Clearance:; _CLEARED by e-mail_______________________________ Christian Barratt, Deputy Mission Director; 4/11/2019_____ Date. Approval:; _______________________________________________ Jene Thomas, Mission Director; ______________ Date.

CC: DMann

BLANK PAGE

Environmental Mitigation and Monitoring Plan (EMMP) Narrative

1.	Background, Rationale and Results Expected:

The overarching objective of the USAID Water and Sanitation Project (“the Project”) is to increase access to safe drinking water and safely managed sewage services in Haiti.  The Project serves to build operational effectiveness and solvency of Haitian water utilities, Centres Technique d’Exploitation (CTEs) and their regional administrators Les office régionale de l’eau potable et de l’assainissement (OREPAs) to enable sustainable service delivery. Specifically, the project will focus on increasing access to water supply and sanitation services (WSS) in three communes, Cap-Haitien, Mirebalais and Croix-des-Bouquets–(Canaan), identified by the Government of Haiti as priority cholera “hotspot”, and two communes, Les Cayes and Jeremie, whose water and sanitation infrastructure sustained major damages from Hurricane Matthew, while simultaneously building the enabling environment to sustainably expand these services. Working in these locations, the project aims to enable 250,000 people to gain access to new or improved water services and 75,000 people to gain access to basic or safely managed sanitation services.

The project is organized in three mutually reinforcing components to support its objectives:

- Component 1. Increased access to sustainable water supply services,

- Component 2. Increased access to sustainable sanitation services, and

- Component 3. Strengthened enabling environment for sustainable delivery, operation, and maintenance of water and sanitation services.

Additionally, the USAID Water and Sanitation Project manages an Enterprise Acceleration Fund (EAF), that offers grants or sub-awards to help expand safe water and sanitation services, and accelerate impact and innovations by locally established entrepreneurs in the sector, increasingly integral to sustainable water and sanitation service delivery.

2.  Activity Description:

The present EMMP is for the project’s second, small-scale Quick Impact Project (QIP). It is in the Les Cayes commune and is called the Charpentier Pumping Station QIP. The QIP will consist of installing two solar-powered pumping systems at the Centre Technique d’Expoitation’s (CTE – public water utility) pumping station at Charpentier.

Currently, the Les Cayes water network is supplied by the Charpentier pumping station (please see Figure 1 below for a detailed map of the site), not far from the city’s residential district near Avenue Quatre Chemins. The station has six boreholes drilled in 2009, four of which are equipped with submersible pumps. The characteristics of the current pumps are:

- One old submersible, 40 HP pump, generating a total flow rate of 40 l/s in the F1 borehole well,

- Two new submersible pumps in the F3 and F4 borehole wells – they are 100 horsepower pumps powered by three-phase, 480 volt electricity, and pump water at a rate of 64 l/s (F3) and 76 l/s (F4), and

- A solar-powered pump with a flow rate of 12.62 to 37.85 l/s (depending on the supply of solar energy) in the F5 borehole well (the system was set up to provide an average of 29 l/s).

The pump system takes water from the upper water table from a depth of 42 to 70 m, while the F1, F2, F3 and F5 wells feed an existing 300 m3 steel water tank on site (see Figure 5 below for a photograph of the tank). The tank has recently been rehabilitated and is equipped with an inlet pipe, a 300 mm diameter cast iron drain pipe, and all the associated valves.

The F5 borehole solar pump can fill the 300 m3 tank in approximately five hours.  Once the tank is full, however, because of high usage, it empties in less than 45 minutes.  The population served by the Les Cayes water network is approximately 17,500 people (and rapidly growing) and the capacity of this single, solar-powered pump is insufficient to meet the current and future water demands. The CTE is therefore obliged to purchase costly diesel fuel for the 400 W on-site generator that supplies all the electrical demands at Charpentier to operate the pumps to partially meet the water demands of the population.

A second 700 m3 capacity tank, connected to the F4 borehole – located 3 km away from the F5 well – is currently in the final stages of rehabilitation to improve water pressure throughout the network.  This tank, elevated, and with an original capacity of 600 m3, was built in 1980 of welded steel on a reinforced concrete frame in close proximity to a swampy area at the eastern end of the city. The tank was out of commission for a number of years due to structural safety issues caused by corrosion.  In 2018, it was rehabilitated and its capacity was increased to 700 m3 to improve service delivery.

The pumping station is run by the Centre Technique d'Exploitation Sud (CTE Sud), Haiti’s Water Utility for the South of the country. CTE operations are overwhelmed by insufficient maintenance and a lack of planning and empowered personnel. The CTE operations are managed by four key staff: one electromechanical technical manager, one electromechanical operator and two general operators. Based on the CTE’s financial records, operation and maintenance costs totaled 16,857,684 HTG during the 2018 fiscal year (Oct. 2017-Sept. 2018). These costs consist mainly of salaries and other staff-related costs, debt payments, maintenance and transportation. According to the records reviewed by the USAID Water and Sanitation Project team, the total collected revenue for the same period amounted to 12,713,685 HTG, reflecting a deficit of 4,143,999 HTG. The cost recovery rate is approximately 75%. Overall, the proficiency of operations at the site, although much higher than the average CTE operations, can be improved and used as a performance model.

Although the site is protected by an armed security guard at the entrance, the site’s perimeter fence will need to be heightened with barbed wire placed at the top to improve security. Operational oversight at the station also needs to be improved, with regularly scheduled inspections, cleaning and maintenance (broken equipment and hydraulic parts are strewn around the site and need to be stored securely).  The disorderly condition of the site obscures important operational issues that could be flagged during inspections and generally reflects a low standard of management. The poor state of site management at Charpentier is partially due to the fact that there is only one caretaker maintaining the relatively large enclosure. In the past, day-workers were hired to assist the caretaker with cleaning, but more recently the CTE has not been able to hire due lack of cash flow, exacerbated by the high cost of fuel for the generator (see more information below on the CTE’s finances). Information on the neighborhood surrounding the pumping station is provided in Section 3 – Site Location and Land Use, below.

The piped water network of Les Cayes is divided into three sectors. The current network includes about 60 km of pipes of different diameters and thirteen (13) kiosks built on the outskirts of the city. According to the CTE, the total number of subscribers in Les Cayes is 5,122, of whom 2,800 are active and 2,322 are inactive. The network is currently fed by a 300 m3 reservoir with another reservoir of 700 m3 currently being completed and soon to come on line in the Savannah area of town.

Currently, the CTE provides water service only once every two days to each sector. The CTE uses the services of the public energy utility, Électricité d’Haïti (EDH), via a three-phase transformer bank of 300 KVA as a source of energy for the pumping station, and a 400 KW generator as a backup source. Along with EDH’s inability to supply electricity during regular hours, and the accumulation of CTE debts to EDH, the CTE instead uses their generator on a daily basis for pumping. This requires an exorbitant amount of diesel fuel. Due to the high cost of fuel for the generator (about 400,000 HTG/month), and monthly electricity bills from EDH that vary from 750,000 to 800,000 HTG, the three sectors for which the CTE is responsible to supply water only receive water on a sparse basis. Also, as noted above, the F5 solar pump only partially provides the water that the CTE needs to cover the generator fuel gap.

By replacing the F1 and F2 pumps with solar-powered pumps with the same capacity as the F5 pump, the CTE’s fuel purchase costs will be significantly reduced. The 300 m3 reservoir that currently fills in 5 hours via F5 will be able to be filled in about 3 hours. This will allow two of the network’s sectors to be fed during the day using the solar-powered pump. The large downtown sector of the network will be fed during the evening by the use of the diesel-fuel generator or on-grid EDH electricity. The following day, one of the solar pumps would be used in combination with the generator (to power one of the 100 HP pumps) to directly pump to the new 700 m3 savanna reservoir. This alternate-day approach will be imperative in order to serve the large city center and maintain adequate pressure for this sector.

Overall, the QIP’s installation of two solar-powered pumps for the F1 and F2 borehole wells will improve the system in the following ways:

- Pumping from the new solar-powered pumps will partially compensate for the high cost of fuel; this will effectively reduce the operating costs for producing/pumping water for the city of Les Cayes.

- In addition, this will allow for a 41% increase in water production and more frequent water distribution to the three sectors and will also increase revenue for the CTE. This increase is calculated as follows: total current production of the system is 170 l/s; installation of the QIP’s two, new solar-powered pumps will increase production by 70 l/s, yielding a total potential production of 240 l/s which represents a 41% increase.

- The more frequent water distribution is estimated at twice a day for each of the three sectors; this is expected to result in improved (more reliable) water for the 3,500 households (or 17,500 beneficiaries) currently serviced by the system.

Details of the proposed activities and tasks associated with this QIP follow. This work will be carried out via a subcontract with a local general contractor (with experience in drilling, water supply pumps, solar power, and electrical installations).

- Quality control of the F1 and F2 borehole well water before and after the QIP work; this will essentially consist of a basic water quality test of samples from the wells at Haitian and American laboratories and will help calibrate chlorine dosing levels; samples taken at the end of QIP activities will help ensure that no major water quality issues have emerged during the repairs and rehabilitation; laboratory analyses will also contribute to the water safety plan for the Les Cayes water network.

- Supply and installation of complete solar-powered pump systems; this will include installing two 6'', 25 horsepower pumps, a control cabinet, stainless steel drainage pipes, and various associated hydraulic parts (manometer, suction cup, stilling tube, well probe, cable splice kit, grounding rod, surge protector, safety rope, pressure sensor, float switch and various parts associated with the photovoltaic system: protector, combiner, disconnector, and sun switch).

- Supply and installation of the photovoltaic system, including poly, 330-watt panels, frames, raised supports, and electrical connections; the total number of panels to be supplied is 190: 85 will be installed in close proximity to F1, 85 in close proximity to F2, and the remaining 20 will be stored as spare parts; the dimensions of each panel are 1950 mm (length) x 990 mm (width) x 40 mm (height or thickness); see Figure 1 for the approximate location of the panels within the Charpentier pumping station. The surface area of each individual panel is about 1.9 m2; the total surface area for an array of 85 panels needed to power each pump is about 164 m2.

- Construction of two strong metal structures to support the panels (see Figure 2 below for a depiction of the layout of the panels; also, see section 7 below for information on design specifications related to hurricane-force winds).

- Connection of the discharge line of the new pumps to the existing discharge line.

- Supply and installation of the backflow prevention valve system.

- Repair of the system’s chlorinator: this will consist of replacing the agitator, reconditioning the unit, and repairing piping leaks.

- Securing and protecting the pumping station site by raising the fence (from 2.5 to 3.5 m); and installing barbed wire on top; the fence will be made of bricks.

- General cleaning of the site; this will include weeding, picking up and taking viable spare parts to the secure storage unit, disposal of non-functional spare parts, and disposal of old, non-functional vehicle frames and parts.

- Storage of spare parts in a secure place and supplying use or in/out inventory logs.

Associated Technical Assistance

USAID Water and Sanitation Project staff, supported potentially by Short-Term Technical Assistance/Long-Term Technical Assistance, will develop an operations manual for the site and will train CTE staff (principally, the 4 staff noted above) on improved site and equipment maintenance as well as enhanced record-keeping (filling out and archiving logs, etc.).

Actions related to operations and maintenance (O&M) training, which will build the capacity of CTE staff, include:

- Develop pumping logs

- Develop chlorination operation and water quality testing logs

- Develop material use and fueling logs (this will include generator noise management)

- Develop daily repair, incident and activity logs

- Develop site inspection checklists (this will include water table monitoring)

- Develop long-term plan to ensure water supply

- Develop Site Operations Manual which will include details on:

  - Materials storage

  - Fueling and storage

  - Generator use and noise management (this will include recommendations on moving office and caretaker bedroom from the generator building and constructing a canopy or enclosure around the generator)

  - Water table monitoring

  - Long term planning to ensure water supply

  - Measures to address climate variability (including flooding and hurricanes)

  - Cleaning

  - Access control

  - Trash management

  - Boundaries (private/public areas)

  - Prohibited actions (cooking, sanitation, livestock, vehicle storage, fuel, etc.)

- Develop emergency repair contacts

- Develop and implement a training program focused on use of/implementation of operations manual, as well as all logs and checklists

Training for the CTE will target the following staff:

- the operations team leader,

- the maintenance manager,

- the laboratory manager, and

- the quality control officer.

Figure 1: Charpentier Pumping Station site plan (showing location of solar panels for F1 & F2 pumps).

Figure 2: Depiction of solar panel layout with metallic support structure.

Figure 2: Depiction of solar panel layout with metallic support structure.

3.	Environmental Baselines:

Site location and land use

The QIP site is located in the Charpentier quarter within the urban area of the Commune of Les Cayes (southwest quadrant of Haiti). The site is a pumping station for the CTE (as described above) and is called the Charpentier Pumping Station throughout this document. It can be accessed via an unpaved road connected to the Route National number 2 (RN2) which is about 300 meters to the south. As shown in Figure 3 below, the QIP site is surrounded by houses and other buildings. These houses or residences may be affected by dust and noise that will be generated during the QIP activities. Some non-residential buildings (offices, churches, schools, hotels and small shops) can be found along the main roads near the pumping station. According to the CTE, most of these non-residential buildings are connected to the existing piped water network. They will therefore benefit from the improved water services. These non-residential buildings will also likely be affected by dust and noise from the QIP activities. About 1 km to the southeast of the pumping station, some agricultural plots can be found. These plots are occupied by seasonal crops in association (corn, beans, okra, banana, sugar cane), and in monoculture (usually rice).

QIP Site

QIP Site

Figure 3. QIP site location (OpenStreetMap)

Water resources

The closest permanent water ways to the QIP site are: L’islet River which flows along of the eastern side of Les Cayes’ urban area and La ravine du sud River which flows along the western side (see Figure 4 below). These two rivers can be characterized as having a torrential flow regime. Their flow increases during the rainy seasons (from April to May and from August to October) and decreases considerably during dry seasons. Some flood plain points can be found throughout the Les Cayes area. They often become swamps during the rainy seasons.

In the QIP site area, groundwater is recharged by infiltration of precipitation on the Les Cayes plain and by percolation of the surface water through small natural drains and by groundwater flowing from the karstic areas of the mountainous regions overlooking the plain. According to information provided by the Les Cayes CTE, there are three primary aquifers underlying Les Cayes, including the Charpentier Pumping Station area: these are known as upper, the intermediate and the lower (artesian) aquifers. The upper and intermediate aquifers are difficult to distinguish; they are often confused and referred to as the upper aquifer. The upper aquifer is subject to pollution, especially in built-up areas that have toilets with septic tanks and sumps or simple latrines. The lower aquifer, found at depths between 30 and 80 m, is considered healthy (NORPLAN, 1999; BRL Ingénierie, 2009), and is therefore preferred as a source of drinking water and cooking water. Additional information provided by the CTE follows:

- The first aquifer is very close to the surface (5-10 m deep). It is located, approximately, between 20 and 40 m elevation. It is exposed to coliform contamination due to the presence of a lot of latrines in the area.

- The second aquifer (15-25 m deep) is located, approximately, between 5 and 10 m elevation. It is also exposed to contamination. The results of a series of analyses conducted in 2011 showed that several private wells dug between 20 and 30 m deep in some parts of the city are contaminated with coliform.

- The third aquifer is found at a depth of 30 to 80 m. This is the aquifer that is used by the Les Cayes CTE at the Charpentier Pumping Station. The water quality tests which will be conducted for the QIP work will allow a determination regarding if this aquifer is also affected by coliform contamination or not.

QIP site

QIP site

Figure 4. Les Cayes area showing main permanent water ways

Topography and Soils

Located on the coastal plain, the QIP site area is very flat. This increases the vulnerability of this area to flooding. As is generally the case for areas with such topography, the soils are mainly alluvial. Some hydromorphic soils can also be found in the swampy areas.

Noise

At the Charpentier Pumping Station, the main existing noise source is the diesel generator currently used to power the pumps and other generators in the area used by commercial and residential establishments. The noise generated may not significantly affect the wellbeing of the nearby communities, but it may affect the site employees (and workers during QIP implementation), especially since there is a technical office and a room for the housekeeper in the generator building. During a recent field visit, the level of noise measured in the technical office was above 90 dB (the pain threshold).

Air quality

There is no monitoring system for air quality in Les Cayes. In the vicinity of the QIP site, the dust and emissions generated by traffic and the pumping station’s generator could affect the air quality. This risk will be increased by vehicles delivering materials and equipment during the QIP work. The soot produced by the generator will also require more frequent cleaning of the solar panels (to maintain optimal performance).

Flora

In terms of percentage of area occupied, there is predominance of seasonal crops in the Charpentier Pumping Station yard. There are also some scattered fruit trees (mango, tropical-almond, breadfruit) in the yard. These fruit trees can be also found in the surrounding areas.

Fauna

The fauna in the area is mainly represented by livestock and domestic animals. Some ducks and chickens were observed in the pumping station yard during the field visit. They also can be found in the surrounding houses’ courtyards. In the nearby agricultural plots, some herbivores (goats, cows, donkeys, horses) were observed. Some reptiles, insects and birds, adapted to human-modified areas, can be found either in the pumping station yard or in the nearby agricultural plots.

4.	Potential Environmental Impacts:

The activities and actions associated with the Les Cayes QIP will have significant positive environmental impacts. These impacts can be summarized as improvement of the water services provided to the local population and a decrease of greenhouse gas emissions (due to reduced generator use). However, the QIP activities will also generate some potential adverse environmental impacts which are mostly short-lived and limited to the QIP implementation period. These potential adverse impacts are principally linked to noise and dust that will be generated during QIP operations, handling and disposal of waste, and risks to human health and safety. Additional details on potential environmental impacts can be found below.

Impacts on water resources

The installation of solar panels for powering the 2 solar pumps will initiate pumping from the borehole wells (F1 and F2) and may draw down water levels, depending on the replenishment rate from the aquifer. We believe, however, that any draw down will be insignificant. Static water table levels at the site are between 0.8 and 1 m; there is also an artesian spring in the middle of the pumping station that is evacuated via an existing ditch. We will also include water table monitoring in the operational plan and O&M training noted above (more information on water table monitoring can also be found below in the climate change integration section). Finally, since these pumps will mainly be operated during the day, the water level will increase again in the borehole wells during the night.

However, when all the pumps of the pumping station are simultaneously operated, the draw down may be significant and could affect the aquifer. However, it should be noted that previous studies (BRL Ingénierie, 2009; COFOR, 2009; NORPLAN, 1999) during the installation of the wells have been conducted and the rates of pumping proposed are based upon acceptable levels of drawdown and interference. The design rates of pumping do not exceed those originally calculated for the site.

Impacts on nearby communities

Multiple metallic rods will be used in building the structure which will support the solar panels. Assembling the structure will require long welding operations. This will increase the ambient noise level for a relatively long period of time. Nearby communities may also be affected by the dust which will be generated during construction of the metallic support structures and the circulation of vehicles that will deliver materials and equipment during QIP activities. Also, the location that will receive the solid waste removed from the site may be polluted.

On the positive side, the installation of the solar panels will increase the Charpentier Pumping Station production (by about 41%). The CTE will be able to supply the water more frequently to the currently connected households and additional households could begin to receive water. In addition, the fuel consumption of the CTE will decrease and its revenue will increase. Finally, cleanup of the pumping station yard will help to prevent illness caused by mosquitos (e.g., malaria, zika, chikungunya).

Impacts on workers’ health

Installing barbed wire at the top of the perimeter fence may cause construction worker injuries. There may be other risks to workers’ health linked to dust, excessive physical effort, lack of proper protective equipment, or a failure to follow proper safety protocols.

Summary table of potential impacts

| Activities | Potential impacts | Impact type | Nature of impact | Environmental components affected | Probability of occurrence |
| --- | --- | --- | --- | --- | --- |
| Construction of metallic support structure for solar panels | Poorer air quality linked to dust produced by circulation of vehicles, and during excavation | D | - | Air | Med |
|  | Increased noise levels | C | - | Workers, Site employees, local population | High |
|  | Poorer health of workers | D | - | Workers | Low |
| Installation of solar panels to power submersible pumps; use of solar-powered pumps | Shock or electrocution of unprotected workers | D | - | Workers | Low |
|  | Draw down of water level in both F1 and F2 borehole wells | D | - | Groundwater |  |
|  | Improvement of water supply to local communities | D | + | Local communities | High |
|  | Reduced diesel fuel consumption & increased CTE revenue | D | + | Les Cayes CTE | High |
|  | Reduced greenhouse and toxic gas emissions | D | + | Air | High |
| Site cleanup/disposal of waste | Reduced disease risk due to elimination of shelter and breeding areas for disease vectors | D | + | Site employees, local communities | High |
|  | Contamination of location that will receive solid waste | D | - | Soil, air and water resources | Med |
|  | Poorer health of workers | D | - | Workers | Low |
| Raising site fence + barbed wire | Improved site security | D | + | QIP site (Charpentier Pumping Station) | High |
|  | Poorer air quality linked to dust produced by circulation of vehicles transporting construction materials | D | - | Air | Med |
|  | Injury of unprotected workers | D | - | Workers | Med |

Legend

D: Direct; 	I: Indirect; 	C: Cumulative

| - | Negative impacts |
| --- | --- |
| + | Positive impacts |

5. 	Environmental Mitigation Measures:

To mitigate the potential adverse impacts mentioned in the preceding section, we propose the following broad mitigation measures (for details on these measures, please refer to Tables 2 and 3 below).

Figure 5: 300 m3 steel water tower in Charpentier pumping station yard.

Figure 5: 300 m3 steel water tower in Charpentier pumping station yard.

- Mark work site and control access;

- Cut off electricity to site during electrical repairs/installation using lockout tagout procedures;

- Submit QIP specifications and design to USAID for approval;

- Monitor water levels in both borehole wells (F1 and F2): daily during QIP work and twice a week subsequently;

- Establish guidelines for pumping duration and adjustments when needed;

- Establish and implement waste and debris management plan for the site;

- Ensure solid waste transport from work site to appropriate dump;

- Wet, sprinkle or dampen well yard grounds and surfaces;

- Ensure or establish and follow adequate worker health and safety procedures or protocols;

- Ensure wearing of proper personal protective equipment; and

- Limit use of equipment and all QIP work activities to normal working hours.

It should be noted that that project’s environmental compliance (EC) team will monitor the construction sub-contractor carrying out the QIP work. The sub-contractor will be responsible for ensuring their workers are aware of the EMMP and follow the listed mitigation measures. This will require some training by the project’s EC team and regular meetings between the sub-contractor and the EC team.

6. 	Gender:

For overall positive water service benefits linked to QIP activities, there is no significant disproportionate effect with respect to men and women. The QIP work will increase the pumping capacity of the Charpentier Pumping Station. Consequently, more water will be available to be supplied to the connected households. In general, this positive impact will benefit men and women equally. It may be more significant for women, because they are the ones who are generally responsible for providing water to households. The women will then have more time to devote to other activities.

With respect to the QIP construction activities, there is a risk of disproportional advantages accruing to men. To ensure women’s participation in relevant tasks, the project will implement the following measures:

- Insert a paragraph encouraging women-led firms to bid in the tender publication document,

- Ensure that women-led firms and men-led firms have equal opportunity to bid, and

- Among qualified companies, prioritize those who have the highest percentage of female employees.

For non-specialized tasks like site cleanup, the project will ensure that the sub-contractor aims to hire at least 50% female workers. The project will also work with the sub-contractor to seek out and hire women for specialized tasks.

7. 	Climate Change Integration:

As required under Executive Order 13677, “Climate-Resilient International Development,” the issues related to climate change have been and will continue to be considered with respect to project activities. This section describes the potential impacts of climate change on the project and vice-versa, with particular attention to the Les Cayes QIP activities.

In general, activities undertaken as part of this QIP will implement measures recommended in the climate risk management matrix appended to the project’s IEE. These include incorporating the following elements into the Charpentier pumping station’s operations manual and associated O&M training:

- Developing a long-term plan to ensure raw water supply,

- New construction incorporating measures to respond to climate variability, and

- Ensuring high quality operations and maintenance.

The increase of the frequency and the intensity of the hurricanes and tropical storms during these last decades is linked to climate change according to some studies. Since the commune of Les Cayes is on the coast and often in the path of tropical storms and hurricanes, the equipment that will be installed during QIP activities will likely be exposed to such devastating meteorological events. The solar panels that will be installed will be the most vulnerable. To address this issue, the project could plant trees along the site fence to constitute a natural windbreak (there is enough space along the fence to plant trees). In addition, project design specifications include consideration of wind loading during extreme events.  Both the final consideration of the height of the structure and the structure’s design will include best available practices to prevent damage from extreme magnitude events. Higher rainfall periods associated with climate change may also cause flooding throughout Les Cayes, including the Charpentier Pumping Station. Management of the station and protection of the borehole wells, pumps, and other equipment during flooding events will be incorporated into the site operations manual.

Design of the solar panel installation and equipment associated with the solar-powered pumps includes hurricane mitigation considerations and has also incorporated recommendations and lessons from the EarthSpark solar array installation damaged by Hurricane Matthew as well as general recommendations based on experience from hurricanes Harvey, Maria and Irma in 2017 and other hurricanes and cyclones (Stuart Dykstra, Sr. Water and Sanitation Expert, pers. comm.). These recommendations will also be incorporated into the pumping station’s operations manual and associated O&M training. These considerations and measures include:

- Through-bolting of supports (as opposed to top-down or T clamps) and frequent checking of bolted connections,

- Ensuring ample open space around solar panels (space cleared of large trees or palms),

- Frequent pruning of trees and palms within pumping station (removal of large branches and fronds),

- Securing all roofs of all buildings/structures within the pumping station, and

- Using pre-fabricated solar panel racks (NuSolar, 2017).

With respect to flooding, the main considerations that will be incorporated into the operations manual include:

- Maintaining (cleaning) the network of lined drainage canals around the pumping station,

- Protecting the borehole wells from floodwater entry, and

- In the case of any new structures to be built or rehabilitated within the pumping station, elevating these structures to the extent possible.

Climate change may also lead to prolonged dry periods and intense drought. However, the underlying aquifer includes an immense storage capacity due to the geology of the area. Though lowered water levels are likely from reduced recharge of the aquifer during long and intense drought events, adverse depletion of the aquifer is highly unlikely under any future use scenario. To address this concern, the project will include management of drought periods in the site operations manual, and will work with the CTE to establish guidelines, including monitoring and, potentially, a modified pumping schedule during drought periods if reduction in water tables exceeds a threshold value. However, based on conversations with the CTE staff, historical water table levels and previous design of pumping regimes, over-exploitation of the aquifer is extremely unlikely. It should also be noted that the water table will be closely monitored via transducers in each borehole well and information transmitted from the transducers to the pumping station’s control panel. The operations manual guidelines will also include measures to reduce water loss due to improper equipment operation or lack of equipment maintenance.

It is also important to mention that some of the QIP activities may contribute to climate change. The circulation of vehicles during QIP work will generate a certain quantity of CO2 (the most abundant greenhouse gas). To address this issue, the project could consider planting trees in and around the pumping station yard (there is enough space in the yard to plant trees); these trees will sequester carbon and offset some of the greenhouse emissions associated with using vehicles during QIP activities. An even larger offset will occur due to the reduced use of water trucks once the station is fully operational. Finally, it is important to note that the installation of the solar panels will help to decrease the pumping station’s greenhouse gas emissions by significantly reducing use of the diesel generator; this can be construed as a highly positive contribution to climate change mitigation.

References

BRL Ingénierie. 2009. Complément d’étude et maitrise d’oeuvre pour la réalisation des travaux de réhabilitation et d’exécution du système d’alimentation en eau potable de la ville des Cayes. BRL Ingénierie: Nîmes, France.

COFOR. 2009. Dossier technique des forages de reconnaissance. COFOR (now Entrepose): Colombes, France.

Louis Berger Group Inc. & CECOM Consultants, SA. 2006. Actualisation des études de faisabilité pour la réhabilitation et l’extension du réseau d’eau potable des Cayes et pour la mise en place de système pilote d’assainissement. Louis Berger Group: Morristown, New Jersey.

NORPLAN. 1999. Plan directeur portant sur les études de faisabilité quant à la réhabilitation et à l'expansion du système d'eau potable de la ville des Cayes. NORPLAN: Sandvika, Norway.

NuSolar. 2017. NuSolar PV ground mount kits: Installation manual. NuSolar: Auburn, California.

Environmental Screening Form (Table 1)

|  |  | Column A |  | Column B (answer if you checked “yes”) |  |
| --- | --- | --- | --- | --- | --- |
|  |  | YES | NO | High Risk (difficult to mitigate impact) | Medium Risk (can be properly mitigated) |
| INFRASTRUCTURE (Buildings, roads, WASH, etc.) |  |  |  |  |  |
| 1 | Will the intervention involve construction and/or reconstruction/rehabilitation of any type of building? For new construction, if less than 1,000 m2 = medium risk, if greater than 1,000 m2 = high risk. | x |  |  | x |
| 2 | Will the intervention involve building penetrating roads, road rehabilitation and maintenance or other road related infrastructure (drainage, bridges, etc.)? If penetrating road construction/rerouting = high risk2, if repair/rehabilitation (improving drainage, resurfacing of existing roads) = medium risk. |  | x |  |  |
| 3 | Will the intervention involve construction or rehabilitation of water and sanitation infrastructure (irrigation systems, potable water, water harvesting, septic systems etc.). Potable water systems require testing for bacteria, arsenic and other heavy metals. | x |  |  | x |
| 4 | Will the intervention involve construction or rehabilitation of any other infrastructure such as landfills, incinerators, energy infrastructure, etc. | x |  |  | x |
| 5 | Will the intervention involve any kind of construction at all and/or engineering design? If YES, then a USAID Engineer must approve designs per USAID/Haiti Mission Order #36. | x |  |  | x |
| 6 | Does the intervention require adherence to national building code or other regulatory standards? Mitigation measures in Table 2. |  |  | N.A. | N.A. |
| 7 | Does the intervention require local or national planning permissions (i.e. zoning, building permits, etc.) |  |  | N.A. | N.A. |

| BIOPHYSICAL |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 8 | Will the intervention involve the use of pesticides of any kind? |  | x |  |  |
| 9 | Will the intervention involve changes in water quality (pollution, sedimentation, stagnation, salinization, temperature change, etc.) |  | x |  |  |
| 10 | Will the intervention affect surface or groundwater quantity | x |  |  | x |
| 11 | Will the intervention involve training and/or implementation of agricultural practices/production including animal husbandry? |  | x |  |  |
| 12 | Will the intervention involve aquaculture systems? |  | x |  |  |
| 13 | Will the intervention involve the use or disposal of hazardous materials (used engine oil, paint, varnish, lead-based products, fluorescent light bulbs/mercury, batteries, asbestos or other hazardous or special management waste)? Consider effects to both the biophysical environment and human health. |  | x |  |  |
| 14 | Will the intervention involve implementation of timber management, extraction of forest products, clearing of forest cover, and/or conversion of forest land by cutting of trees >20cm diameter at base height (DBH)? |  | X |  |  |
| 15 | Is the intervention in or near (within 50m) any sensitive terrestrial or aquatic areas including protected areas, wetlands, critical wildlife habitat (including nesting areas), and threatened or endangered species? |  | X |  |  |
| 16 | Will the interventions proposed generate airborne particulates (dust), liquids, or solids (i.e. discharge pollutants) or potentially violate local air standards? | x |  |  | x |
| 17 | Will the intervention create objectionable odors? |  | X |  |  |
| 18 | Will the intervention occur on steep slopes (greater than 15%)? |  | X |  |  |
| 19 | Will the intervention contribute to erosion? |  | X |  |  |
| 20 | Will the intervention change existing land use in the vicinity? |  | X |  |  |
| 21 | Is the proposed intervention incompatible with land type (i.e., annual crops on steep slopes, infrastructure on poorly drained soils)? |  | X |  |  |
| 22 | Will the intervention affect unique geologic or physical features? |  | X |  |  |
| 23 | Will the intervention have potential effects to inhabitants, natural landscapes, or flora/fauna downstream from the intervention site? |  | X |  |  |
| 24 | Will the intervention have a direct or indirect effect, or include actions with mangroves, coral reefs and other marine/coastal ecosystems? |  | X |  |  |
| GLOBAL CLIMATE CHANGE |  |  |  |  |  |
| 25 | Are interventions or outcomes vulnerable to changes in the weather or climate such as changes in precipitation patterns, increased temperatures or sea level rise? | x |  |  | x |
| 26 | Does the intervention exacerbate climate change vulnerabilities (i.e., drought, flooding, decrease water supply)? | x |  |  | x |
| 27 | Will the intervention create greenhouse gas emissions from decomposing waste, burning of organic matter, or use of fossil fuels etc. (consider duration and scale) | x |  |  | x |
| SOCIO ECONOMIC |  |  |  |  |  |
| 28 | Will the intervention contribute to displacement of people, housing or businesses? |  | x |  |  |
| 29 | Will the intervention affect indigenous peoples and/or unique cultural or historical features? |  | x |  |  |
| 30 | Will the intervention expose people or property to flooding? |  | x |  |  |
| ENVIRONMENT & HEALTH |  |  |  |  |  |
| 31 | Will the intervention create conditions encouraging an increase in illness, diseases, or disease vectors (waterborne, STDs or other)? |  | x |  |  |
| 32 | Will the intervention generate hazards or barriers for pedestrians, motorists or persons with disabilities? |  | x |  |  |
| 33 | Will the intervention involve the use, storage, handling or disposal of syringes, gauzes, gloves and other biohazard medical waste? |  | x |  |  |
| 34 | Will the intervention expose workers to occupational hazards? | x |  |  | x |
| 35 | Will the intervention increase existing noise levels? | x |  |  | x |
| GENDER |  |  |  |  |  |
| 36 | Does the intervention inhibit the equal involvement of men and women? |  | x |  |  |
| 37 | Do the intervention results disproportionately benefit/impact men and women? |  | x |  |  |
| OTHER |  |  |  |  |  |
| 38 | Does the intervention/activity involve a sub-award component? |  |  | N.A. | N.A. |
| 39 | Is an operations and maintenance plan required? (generally applies to infrastructure, equipment, road rehabilitation, or water and sanitation action = Yes) | x |  |  | N.A. |

| RECOMMENDED ACTION (Check Appropriate Action): |  | (Check) |
| --- | --- | --- |
| (a) | The intervention has no potential for significant effects on the environment. No further environmental review is required. |  |
| (b) | The intervention includes mitigation measures and design criteria that if, applied will avoid a significant effect on the environment. EMMP Required. | x |
| (c) | The intervention has potentially significant adverse environmental effects; therefore, an Environmental Assessment is required to gather additional analysis before implementation may begin. NOTE: This may apply if any potential effects listed above are marked as “High Risk.” |  |
| (d) | The intervention has significant adverse environmental effects that cannot be mitigated. Proposed mitigation is insufficient to eliminate these effects and alternatives are not feasible. The intervention is not recommended for implementation. *For sub awards, do not fund. |  |

Environmental Mitigation Table (Table 2)

| # of the ques-tion from Table 1 | Action or component with the different tasks required to implement the action. | Description of Impact | Environmental Mitigation Measures |
| --- | --- | --- | --- |
| 1, 3, 4, 5, 16, 34, 35 | Action/task: All tasks associated with site improvement or cleanup Action/task: All tasks associated with the construction of the metallic support structure for solar panels Action/task: Installation of solar panels to power F1 and F2 pumps Action/task: Installation of solar-powered pumps & accessories in F1 & F2 borehole wells Action/task: All tasks associated with raising the site fence and install barbed wire | - Injury to local population if they wander on to work site during construction, rehabilitation, and cleanup actions - Poor workers’ health - Injury of unprotected workers - Increased noise levels - Generation of airborne particulates (dust) - Use of wrong materials due to inappropriate specs/design | (1) Cordon off/mark site before and during the duration of QIP activities, and ensure that no unauthorized personnel access the site; (2) Ensure basic personal protection equipment (PPE), e.g., hardhats, is worn by all workers during QIP work; (3) ensure hired subcontractor firm has adequate Health and Safety (H&S) protocols and procedures and that workers are trained in these protocols/procedures; if not, collaborate with subcontractor to develop procedures and associated training for workers; (4) Limit QIP activities to normal working hours; (5) Wet or dampen pumping station yard grounds and the unpaved access road before the delivery of materials and equipment; (6) Submit QIP specification and design documents to USAID for approval |
| 10, 26, 34 | Action/task: Installation of solar panels to power F1 and F2 pumps Action/task: Installation of solar-powered pumps & accessories in F1 & F2 borehole wells Action/task: Increasing pumping duration once solar-powered pumps are active | - Draw down of water levels in both F1 and F2 borehole wells (groundwater availability) - Shock or electrocution during electrical work | (7) Conduct frequent monitoring of the water levels in both the F1 and F2 borehole wells and adjust pumping regimes as necessary; (8) Include detailed guidelines on pumping duration and adjusted regimes in the Site Operations Manual and CTE training sessions; (9) Ensure electric power supply to all parts of pumping station yard is turned off during solar panels installation and other electrical work using lockout tagout procedures; |
| 13 | Action/task: All tasks associated with site improvement or cleanup | a) Pollution of site or solid waste dump from existing solid waste in the yard and solid waste generated during QIP activities | (10) Establish and implement a waste management plan for the pumping station yard, including during and after QIP work |
| 25 | Action/task: Increasing pumping duration once solar-powered pumps are active | a) Lack of adequate water during drought events | (see mitigation measures numbers (7) and (8) above) |
| 27 | Action/task: All tasks associated with transport of equipment and materials to site as well as transport of solid waste from site to solid waste dump | a) Greenhouse gas emissions | (11) Establish efficient transport schedule with construction sub-contractor to limit the number of trips to and from the site |
| 3, 4, 13, 34, 39 | Action/task: All tasks associated with equipment operation and maintenance; all tasks associated with site maintenance | a) Solid waste accumulation b) Water contamination c) Increased operational costs | (12) Provide adequate and periodic training to CTE staff operating this facility (13) Evaluate staff performance periodically |

Environmental Monitoring Table (Table 3)

REPORTING NOTE: Implementing partners are required to report on this EMMP by submitting updated versions of Table 3 and any relevant narrative in all performance reports that are required in the relevant agreement.  Generally, this includes quarterly and annual performance reports.

| Program, Project, and/or Activity: | USAID Water and Sanitation Project |  |  |
| --- | --- | --- | --- |
| Award Number: | AID-OAA-1-14-00049/720521 |  |  |
| Monitoring Period or Quarter: |  | Date: |  |

| # | Description of Mitigation Measure (same as in Table 2) | Responsible Party for implementing and monitoring mitigation measures | Monitoring Methods |  |  | Estimated Cost of implementing mitigation measures and monitoring | Results |  |  | Recommended Adjustments |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Indicators of implementa-tion | Methods | Frequency |  | Dates Monitored | Problems Encountered | Mitigation Effectiveness |  |
| 1 | Cordon off/mark site before and during the duration of QIP activities, and ensure that no unauthorized personnel access the site | Sub-contractor (impl.); Project EC team (monitoring) | Work site marked; presence or absence of unauthrzd. personnel | Work site monito-ring | Daily for subk; Twice a week for EC team | cf. Proj. staff salaries & subk budget | 1 |  |  |  |
|  |  |  |  |  |  |  | 2 |  |  |  |
|  |  |  |  |  |  |  | 3 |  |  |  |
|  |  |  |  |  |  |  | 4 |  |  |  |
| 2 | Ensure basic personal protection equipment (PPE), e.g., hardhats, is worn by all workers during QIP work | Sub-contractor (impl.); Project EC team (monitoring) | Presence or absence of hardhats | Work site monitoring | Subk daily; Twice a week for EC team | cf. Proj. staff salaries & subk budget | 1 |  |  |  |
|  |  |  |  |  |  |  | 2 |  |  |  |
|  |  |  |  |  |  |  | 3 |  |  |  |
|  |  |  |  |  |  |  | 4 |  |  |  |
| 3 | Ensure hired subcontractor firm has adequate Health and Safety (H&S) protocols and procedures and that workers are trained in these protocols/procedures; if not, collaborate with subcontractor to develop procedures and associated training for workers | Sub-contractor & Project engineering team (impl.); Project EC team (monitoring) | Existence of H&S procedures; site H&S records | Inspection of documents and records | Once (for procedures); twice a week (H&S records) | cf. Proj. staff salaries & subk budget | 1 |  |  |  |
|  |  |  |  |  |  |  | 2 |  |  |  |
|  |  |  |  |  |  |  | 3 |  |  |  |
|  |  |  |  |  |  |  | 4 |  |  |  |
| 4 | Limit QIP activities to normal working hours | Sub-contractor (impl.); Proj. EC team (monitoring) | Absence of work outside of normal working hours | Work site monitoring | Subk daily; EC team weekly | cf. Proj. staff salaries & subk budget | 1 |  |  |  |
|  |  |  |  |  |  |  | 2 |  |  |  |
|  |  |  |  |  |  |  | 3 |  |  |  |
|  |  |  |  |  |  |  | 4 |  |  |  |
| 5 | Wet or dampen well yard grounds and the unpaved road before the delivery of materials and equipment | Sub-contractor (impl.); Proj. EC team (monitoring) | Wet or damp grounds | Work site monitoring | Subk as needed; EC team twice a week | cf. Proj. staff salaries & subk budget | 1 |  |  |  |
|  |  |  |  |  |  |  | 2 |  |  |  |
|  |  |  |  |  |  |  | 3 |  |  |  |
|  |  |  |  |  |  |  | 4 |  |  |  |
| 6 | Submit QIP specification and design documents to USAID for approval | Proj. engineering team | Existence of documents | Inspection of documents | Once (prior to commcmt. of subk work) | cf. Proj. staff salaries | 1 |  |  |  |
|  |  |  |  |  |  |  | 2 |  |  |  |
|  |  |  |  |  |  |  | 3 |  |  |  |
|  |  |  |  |  |  |  | 4 |  |  |  |
| 7 | Conduct frequent monitoring of the water levels in both the F1 and F2 borehole wells and adjust pumping regimes as necessary | Sub-contractor (impl.); Proj. EC team (monitoring) | Monitoring records | Inspection of records | Subk as needed; EC team twice a week | cf. Proj. staff salaries & subk budget | 1 |  |  |  |
|  |  |  |  |  |  |  | 2 |  |  |  |
|  |  |  |  |  |  |  | 3 |  |  |  |
|  |  |  |  |  |  |  | 4 |  |  |  |
| 8 | Include detailed guidelines on pumping duration and adjusted regimes in the Site Operations Manual and CTE training sessions | Proj. engineering team | Existence of Site Operations Manual & content; training records | Inspection of Site Operations Manual and training records | Once for Site Operations Manual; weekly (once training begins) | cf. Proj. staff salaries | 1 |  |  |  |
|  |  |  |  |  |  |  | 2 |  |  |  |
|  |  |  |  |  |  |  | 3 |  |  |  |
|  |  |  |  |  |  |  | 4 |  |  |  |
| 9 | Ensure electric power supply to all parts of pumping station yard is turned off during solar panels installation and other electrical work using lockout tagout procedures; | Sub-contractor (impl.); Proj. EC team (monitoring) | Site health & safety records | Inspection of records | Subk as needed; EC team twice a week | cf. Proj. staff salaries & subk budget | 1 |  |  |  |
|  |  |  |  |  |  |  | 2 |  |  |  |
|  |  |  |  |  |  |  | 3 |  |  |  |
|  |  |  |  |  |  |  | 4 |  |  |  |
| 10 | Establish and implement a waste management plan for the well yard, including during and after QIP work | Sub-contractor (impl.); Proj. EC team (monitoring) | Existence of plan; implementation of measures in plan | Inspection of plan; work site monitoring | Once (for plan); twice a week (impl. of plan) | cf. Proj. staff salaries & subk budget | 1 |  |  |  |
|  |  |  |  |  |  |  | 2 |  |  |  |
|  |  |  |  |  |  |  | 3 |  |  |  |
|  |  |  |  |  |  |  | 4 |  |  |  |
| 11 | Establish efficient transport schedule with construction sub-contractor to limit the number of trips to and from the site | Sub-contractor (impl.); Proj. EC team (monitoring) | Existence of schedule | Work site monitoring | Once (for sched.); twice a week (impl. of sched.) | cf. Proj. staff salaries & subk budget | 1 |  |  |  |
|  |  |  |  |  |  |  | 2 |  |  |  |
|  |  |  |  |  |  |  | 3 |  |  |  |
|  |  |  |  |  |  |  | 4 |  |  |  |
| 12 | Provide adequate and periodic training to CTE staff operating this facility | Proj. engineering & capacity building teams | Training records and site operations records | Inspection of training and operations records | Twice a week during training; monthly after trainings | cf. Proj. staff salaries | 1 |  |  |  |
|  |  |  |  |  |  |  | 2 |  |  |  |
|  |  |  |  |  |  |  | 3 |  |  |  |
|  |  |  |  |  |  |  | 4 |  |  |  |
| 13 | Evaluate staff performance periodically | Proj. capacity building team | Site operations records | Operations records | Every 6 months after initial training | cf. Proj. staff salaries | 1 |  |  |  |
|  |  |  |  |  |  |  | 2 |  |  |  |
|  |  |  |  |  |  |  | 3 |  |  |  |
|  |  |  |  |  |  |  | 4 |  |  |  |

This is calculated by multiplying the number of households by 5, i.e., 5 people per household on average.

Tested parameters will include Electrical Conductivity (EC), TDS, Turbidity, PH, Salinity, Fecal Coliform and E. coli, Total Coliform, Calcium Hardness, Magnesian Hardness, Ammonium (NH4+), Arsenic, Fluoride, Lead, Iron, Sulfate, Nitrite, Nitrate (as NO3), and Residual Chlorine. Initial tests will not include bacterial or Residual Chlorine.

Some of this information also comes from feasibility studies, carried out by NORPLAN, linked to the Master Plan for the rehabilitation and expansion of the drinking water system for the city of Les Cayes.

These analyses include the results of bacteriological analyses, carried out by NORPLAN, on artesian well water in the Charpentier area and an IDB study linked to the master plan of for the rehabilitation and extension of the drinking water system for the city of Les Cayes (BRLi Loan No. 1010 / SF-HA granted by the IDB).

If the system is equipped with batteries, they can store energy and the pumps could be operated after sunset if needed.

The CTE has pending hookup requests that could be connected once the new solar-powered pumps in F1 and F2 are fully operational.